## Sheet1
Estimate for a factory building
Preamble
Surface dimensions of the factory are 105 m x 58 m, with a height of 10 m and a mezzanine floor at 5.0 m. There is no
provision for a basement. Piping and cable are to be suspended from the roof trusses. Aisles will separate the production areas.
The building is virtually windowless to ensure uniform lighting. Background lighting is to be 200 lux, with supplementary
lighting in the machining areas.
Annexes such as offices, facilities outside the building, exterior works, etc., are not included in this price quotation.
a) Earthworks
The earthworks relate only to foundation blocks and strip footings.
b) Drainage
Maximum rainfall is estimated at 250 l/s.ha (0.25 mm/second).
c) Foundations
The structural uprights are set in reinforced concrete foundations, and the posts supporting the façades are bolted to the
external footings.
d) Reinforced concrete skeleton
The mezzanine is to be of reinforced concrete and is intended to house rest and conference rooms.
e) Masonry
The metal sheet façades for the mezzanine section are to be protected by a wall of 19 cm hollow concrete blocks.
f) Steel skeleton
The supporting beams are jointed to the uprights. Vertical wind bracings are to be fitted along the building. The roof
surface is stiffened by a peripheral wind bracing. Roof trusses are suspended from the bottom flange and designed for
a linear overload of 200 daN/m.
g) Flooring
This is designed to resist the overload of a five-tonne fork-lift truck. The reinforced flooring will be laid over 20 cm
ungraded aggregate, and a screed laid on top.
h) Screeds and coverings
The offices and cloakrooms on the mezzanine are floored with PVC tiles over a float-finish screed.
Floors and skirtings of toilets and shower rooms to be covered with vitrified tiles. Walls of toilets and shower rooms to be
faced with ceramic tiles to a height of 2 m.
i) Sanitary installations
Water is distributed from the sub-station.
j) Heating and ventilation
Heating will be by an air system using air heaters supplied with hot water at 90/70° C. Capacity is based on 20° C interior
and -15° C exterior temperature. Air renewal rate: 2.5 volumes/hour.
k) Electrical installations
10 kV electrical current will be stepped down to 400 V by two 630 kVA transformers. The high voltage cells and metering
cells are behind the transformers. Low voltage distribution will be from the same location. Secondary distribution boards are
to be located in the building.
l) Low-voltage equipment
This comprises 25 telephones, 1 intercom with switch and 10 receivers, 1 master clock and 5 slave clocks.
NB: Alternatives are proposed for items: 6 - Steel skeleton and 8 - Heating and ventilation
506-2 Factory building
Your figures
CODE 3 | IT. | ITEM SPECIFICATION | UNIT | QUANTITY | UNIT PRICE | TOTAL PRICE | SUB-TOTAL |  | warning | OBSERVATIONS/ Comments |  | Is Item Priced |  |  | Total | Is Text? |  |  | Total
|  | 1. Earthworks | [6 empty] | notes | from Construction experts |  | 0 | A | B | 0-A | 0 | A | B | 0-A
1.1 |  | Mechanical excavation for strip and independent footings, up to a depth of 2 m below bottom of excavation or ground level; load and dump on site stockpile, up to 300 m away | m3 | 560
1.2 |  | Mechanical excavation for services, drainage and inspection chambers, depth up to 2.5 m, load and dump on site stockpile up to 300 m away | m3 | 1150 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
1.3 |  | Loading and transport of spoil stocked on site, to fill foundation and service trenches and inspection chambers; place in 40 cm layers and compact | m3 | 1368 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
1.4 |  | Additional payment for transport of excess spoil to tip 5 km away. Not including tip charges | m3 | 342
1.5 |  | Supply, place and compact crushed aggregate, diameter 0-60 mm, in 20 cm layers (95% modified Proctor) | m3 | 1306 |  | 0 | TOTAL 1 | 0 | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
2. Drainage
2.1 Concrete drainpipes including connections to inspection chambers
2.1 | a) | 200 mm diameter | m | 120
2.1 | b) | 300 mm diameter | m | 200
2.2 | a) | 150 mm diameter | m | 130
2.2 | b) | 200 mm diameter | m | 25
2.3 |  | Prefabricated concrete inspection chambers with cast iron cover; diameter 1 m, depth 1.75 m | u | 10 |  |  | TOTAL 2 | 0
3. Concrete
3.1 Shallow foundations:
3.1 | a) | N° 1 concrete blinding course, 8 cm | m3 | 20
3.1 | b) | N° 2 concrete | m3 | 85
3.1 | c) | rough formwork | m2 | 420 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
3.1 | d) | reinforcement: HA steel | kg | 5400
3.2 Reinforced concrete joists, staircases, and ramps:
3.2 | a) | Concrete 35N/mm2, 20mm aggregate | m3 | 148 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
3.2 | b) | smooth formwork | m2 | 1184 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
3.2 | c) | reinforcement HA steel | kg | 8245 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
3.3 Grouting of steel skeleton and sealing for anchor holes with cement mortar. Quote price for one upright
3.3 | a) | volume: 10 litres | u | 60
3.3 | b) | volume: 50 litres | u | 20
3.4 Reinforcement concrete skeleton for mezzanine
3.4 | a) | Concrete 35N/mm2, 20mm aggregate | m3 | 70 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
3.4 | b) | smooth formwork | m2 | 490 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
3.4 | c) | reinforcement HA steel | kg | 6650
3.5 Deck
3.5 | a) | Concrete (35N/mm2, 20mm aggregate) ground floor slab, 20cm thick, 150 m² sections, expansion joints, power floated finish with surface hardener | m2 | 6530 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
3.5 | b) | welded mesh reinforcing | kg | 30442 |  | 0 | TOTAL 3 | 0 | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
4. Masonry
4.1 |  | 21.5 cm hollow concrete block walls, including pointing both sides | m2 | 580 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
4.2 |  | 19 cm hollow concrete block walls | m2 | 505 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
4.3 |  | 10 cm solid concrete block partition walls | m2 | 420 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
4.4 |  | 10 cm solid concrete block wall infilling, including pointing both sides | m2 | 243 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
4.5 |  | Rough-cast lean mortar rendering, two skims | m2 | 1550 |  | 0 | TOTAL 4 | 0 | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
5. Metal fittings
5.1 |  | Polyester powder coated aluminium double glazed windows, fixed lights, spacing of uprights approx. 1.10 m, height approx. 1.20 m | m2 | 392 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
5.2 |  | Surcharge for opening lights at 5.1, including opening/closing controls | u | 28
5.3 |  | Polyester powder coated aluminium double glazed windows, opening lights 1.20 m high, 1.50 m wide, overall length 5 m | m2 | 50 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
5.4 |  | Adjustable louvres for automatic ventilation, modules 5.00 x 1.25 m. Polyester powder coated aluminium frame and louvres. Electrically operated. | u | 6 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
5.5 |  | Double-leaf entry doors, 2.00 m x 3.50 m, metal frame, fixed heavy-duty glazed upper light, both leaves security glass | u | 1
5.6 |  | Twin double-skin exterior sliding doors, 2.50 m x 3.50 m, with wicket door, insulated, including girders, rails and guides | u | 4 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
5.7 |  | Double-leaf double-skin interior metal doors, 1 hour fire resistance, 2 m x 3 m, insulated, including frame and furniture | u | 2
5.8 |  | Laminated chipboard interior doors, 0.90 m x 2.125 m, including metal frame and furniture | u | 7
5.9 |  | Double-leaf interior metal doors, single skin, 2.00 m x 2.125 m, including translucent plastic panel | u | 3
5.10 |  | Metal staircase handrail (height 1 m) comprising uprights, rectangular section top rail 40 x 60 x 3 mm and square section bottom rail 40 x 40 x 3 mm | m | 20
5.11 |  | Anodised aluminium roller shutter, 1.80 m x 2.80 m for transformer cells, including locks, channels and frames | u | 2 |  |  | TOTAL 5 | 0
6. Metal framework
6.1 |  | Lattice purlins, 91 units, angle iron section 50/80 mm | kg | 48900 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
6.2 |  | Main lattice beams, 6 units in two pieces, angle iron 90/150 | kg | 62800 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
6.3 |  | Jointed columns including base plates, fixings, anchor plates, stiffeners, test bars and assembly (18 units) | kg | 27700 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
6.4 |  | Various roof frame sections: edging, horizontal rails and beams, vertical bracing, cladding supports, door frames, etc. | kg | 40200 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
6.5 |  | Wind bracings and roofing joists | kg | 15100 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
6.6 |  | Metal framework for partitions | kg | 4900 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
6.7 |  | Twin skin cladding system comprising colour coated steel or aluminium profiled sheeting outer layer, internal liner sheet, insulation to achieve thermal transmission loss not exceeding 0.35 W/m2K including associated flashings and closures | m2 | 2750 |  | 0 |  |  | 0 |  |  | 0 |  |  | 1 | 0 |  |  | 0
6.8 |  | Twin skin roofing panel comprising colour coated steel or aluminium profiled sheeting outer layer, internal liner sheet, insulation to achieve thermal transmission loss not exceeding 0.25 W/m2K including associated flashings and closures | m2 | 6100 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
6.10 |  | Colour coated steel rainwater pipes 225 x 225 mm, 8 units x 10 m | m | 80 |  | 0 | TOTAL 6 | 0 | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
6.11 |  | 2 cm mineral wool suspended ceiling incl. Framework | m2 | 425 |  | 0 | TOTAL 6A | 0 | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
7. Sanitary fittings
7.1 Galvanised steel hot and cold water piping: a) pipework
7.1 | a) | ND 21.3 mm | m | 80
7.1 |  | ND 33.7 mm | m | 140
7.1 |  | ND 48.3 mm | m | 90
7.1 |  | 75 mm diameter | m | 310 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
7.1 |  | ND 88.9 mm | m | 20
b) Insulation (aluminium backed mineral wool, 25 mm)
7.1 | b) | ND 48.3 mm | m | 90
7.1 |  | ND 76.1 mm | m | 310
7.1 |  | ND 88.9 mm | m | 20
7.2 |  | Stopcocks, angled seat, ND 40 | u | 41
7.3 |  | Main cold water supply, including 5 taps, ND 89 mm | u | 1
7.4 |  | Two hot water tanks, 200 l, electric immersion heater, incl. safety valves and connections to electricity, drain and water supply | u | 2
7.5 Water treatment plant, capacity 5 m³/h, consisting of
7.5 | a) | metering pump | u | 1
7.5 | b) | water softener | u | 1
7.6 PVC drainage pipes, surface-mounted
7.6 | a) | ND 50 | m | 45
7.6 | b) | ND 100 | m | 45
7.7 |  | White ceramic WC pan with close-coupled plastic cistern, standard quality, plastic seat and lid, including connections to cold water and downpipe | u | 7
7.8 |  | Wall-mounted urinals, medium quality, including taps and cold water and downpipe connections | u | 6
7.9 |  | White ceramic wash basins, pedestal-mounted, 40 cm x 50 cm including mixer taps and connections to hot and cold water and downpipe | u | 3
7.1 |  | Stainless steel sink (austenitic steel with 18% chrome, 10% nickel), 1.2 m x 0.6 m; two sinks, one draining board, medium quality, including laminated wooden base unit, mixer tap and connections to hot and cold water and downpipe | u | 1
7.11 |  | White enamelled steel shower tray, 90 cm x 90 cm, including taps, shower head, hot and cold water and downpipe connections | u | 8
7.12 |  | Cluster of 10 washbasins in terrazzo, including taps, hot and cold water and downpipe connections and fittings | u | 5
7.13 |  | Floor siphons | u | 5
7.14 |  | Hand-held fire extinguishers (3 kg CO2) | u | 15
7.15 |  | Twin 40 mm fibre hydrants, including cabinets, containing a 30 m hose, one nozzle with sprinkler, one reel, one key, one bucket and hanger | u | 4 |  |  | TOTAL 7 | 0
8. Heating and ventilation
8.1 District heating:
8.1 | a) | steam heat exchangers, 130°/90° C, 6 bar, approximately 1500 kW, including taps and fittings | u | 2 |  | 0 |  |  | 0 |  |  | 0 |  |  | 1 | 0 |  |  | 0
8.1 | b) | local heating sub-station, output 130°/90° C, approximately 3000 kW, including taps and fittings | u | 1 |  | 0 |  |  | 0 |  |  | 0 |  |  | 1 | 0 |  |  | 0
8.2 | a) | air heaters suspended from roof trusses, throughput 7000 m³/h, approximately 80 kW, including roof inlet | u | 20 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
8.2 | b) | frost protection system, including sensor, adjustable control valve and electrical wiring | u | 20 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
8.3 |  | Extractor fans, throughput 7000 m³/h | u | 20 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
8.4 |  | Factory-painted fluted steel radiators, including thermostatic valves and control taps, rated 3 kW | u | 60 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
8.5 | a) | Black steel heating pipe, painted rustproof primer | [7 empty] | Description tidied up- apply to all pipework items
8.5 | a) | ND 33.7 | m | 350
8.5 |  | Diameter 100mm | m | 500 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
8.5 | b) | Heat insulation – mineral fibre insulation, foil faced, 40mm thick
8.5 | b) | ND 33.7 | m | 350
8.5 | b) | for pipe diameter 100mm | m | 500 |  | 0 |  |  | 0 A | Description tidied up- apply to all insulation items |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
8.5 | c) | Butterfly valves, ND 100 mm | u | 20
8.6 |  | Circulating pumps, flow rate 120 m³/h, pressure 2 bar, including 2 ND 133 cut-off valves and expansion joints | u | 2
8.7 |  | Circulating pumps, flow rate 10 m³/h, pressure 0.6 bar, including 2 ND 70 cut-off valves and expansion joint | u | 3
8.8 | a) | feed heads, diameter 300 mm, length 3.50 m, including return header | u | 2
8.8 | b) | 40 mm thermal insulation for feed head, return header | u | 2
8.9 |  | Expansion chambers, volume 900 l, including accessories | u | 2 |  |  | TOTAL 8 | 0
8.1 |  | Outside temperature controlled regulator, including 2 probes (water output and outside temp.), powered stoptap ND 80, 24 hr programme and water and electrical connections | u | 1 |  |  | TOTAL 8A | 0
9. Electrical installations
9.1 High voltage
The various cells are to have single-leaf doors with lock and safety glass inspection panel. Protective covers behind the doors are to prevent accidental contact with live equipment. The connection panels are to be equipped with a set of flat aluminium bars. The commutator bars will be attached to the equipment by means of flexible connectors
9.1 | a) | supply cell - bar set 630 A - isolating switch, manually-operated, 630 A - one load-breaking isolating switch, 630 A - circuit connection and earth switch, interlocking with load- breaking switch - earth bus bar and earth lead for removable socket - neon tube voltage indicator | u | 2 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.1 | b) | metering cell - bar set 630 A - isolating switch 630 A - 3 fuses 6.3 A - 3 voltage transformers, ratio 10000/V-3/100/V-3, 50 VA | u | 1 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.1 | c) | transmission cell - bar set 630 A - load-breaking isolating switch 630 A - 3 current transformers, 50/50 A, 15 VA | u | 1 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.1 | d) | protective cell for each transformer - bar set 630 A - load-breaking isolating switch, 630 A, lever-operated, automatic triggering by fuses - 3 fuses, 20 A | u | 2 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.1 | e) | standby cell - bar set 630 A | u | 1 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.2 |  | Transformers 630 KVA, 10000/400 V, with all fittings, including cabling, terminal boxes, insulating supports lightning conductor, etc. | u | 2 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.3 |  | Principal low voltage distribution unit, comprising: 1 armoured distribution cabinet in painted sheet steel 1 three-phase bar system, 2000 A, in copper with neutral 2 three phase + N circuit breakers, 1200 A, with supply trips 4 3P + N circuit breakers, 630 A, with trips as output to sub- distributors 1 1200 A isolating switch as coupling for second transformer 1 1200 A circuit-breaker for coupling 1 three phase 1000 A (capacitors) 1 set of measuring equipment: | u | 1 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
Each supply set will contain: 3 0-500 V voltmeters 3 ammeters and 1200/5 A current transformers 1 wattmeter for power consumed 1 cosphimeter input indicators alarm indicators
Each output including the coupling system is to contain: 3 ammeters with commutator and 750/5 A current transformer 3 warning lamps
9.4 |  | Automatic correction equipment, 320 kVA, 8 steps, condenser protection, batteries, etc., with all fittings | u | 1 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.5 |  | Steel meter cabinet fitted with watt-hour meter, reactive volt-ampere-hour meter, contact timer, overload monitor with automatic adjustment, overload cut-out, digital print-out, timers, cabling and all fittings | u | 1 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.6 |  | Sheet steel distribution cabinets, type IP 54 protection, for heavy and lighting current (380/220 V, 50 Hz) height: approximately 2200 mm depth: approximately 800 mm width: approximately 2500 mm | u | 4 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
copper bars, 630 A, 5 conductors
Items fitted: 12 three-pole knife switch circuit-breakers for cartridge size 0-3, including 100-500 A cartridges; 12 three-pole sockets or 25 A-63 A fuses complete with fuses and other fittings 1 three-pole switch, 630 A, for power supply; 10 one-pole circuit-breakers, 16 A, for lighting; 7 three-pole circuit breakers, 25 A, for heavy current; 1 voltmeter 0-500 V, with voltage selector
Provision of cable clamps as follows: - one 4 x 240 mm² cable - 30 cables up to 5 x 2.5 mm² - 30 cables up to 4 x 70 mm²
9.7 |  | a) sheet steel distribution cabinet, IP 54 protection, for air heater control unit, central heating pump and controls. The following to be fitted and cabled: all relays, contactors, fuses, switches, pilot lights, 1 time switch programmable for day/night/week, 10 switches for the three-speed ventilator assemblies | u | 1 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
Fittings:
9.7 |  | 1100 m of cable 5 x 1.5 mm² (thermostats) | m | 1100
9.7 |  | 1100 m of cable 7 x 1.5 mm² (air heaters) | m | 1100
9.7 |  | 500 m of cable 4 x 1.5 mm² (other) | m | 500
9.8 |  | NYM cabling, 2 x 1.5 mm², including cable grips | m | 4100 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.9 |  | NYM cabling, 3 x 4 mm², including cable grips | m | 4100 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.1 |  | NYM cabling, 5 x 16 mm², including cable grips | m | 475
9.11 |  | NYM cabling 4 x 35 mm², including cable grips | m | 475 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.12 |  | Prefabricated electrical conduits current 100 A, circuits: 4conductors + earth (5 x 27 mm²) | m | 100
9.13 |  | Couplers (junction boxes): current: 40 A with cartridges | u | 4
9.14 |  | Power supply box (output): rating 100 A | u | 15
9.15 Lighting
9.15 | a) | fluorescent ceiling lights with reflector, length 2 m, 2 x 215 W, 380 V | u | 78 |  | 0 |  |  | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
9.15 | b) | ceiling lights, sealed, length 1.20 m, 1 x 65 W, 220 V | u | 12
9.15 | c) | ceiling lights for offices, etc., 2 x 65 W, 220 V | u | 49
9.16 Supplementary fittings
9.16 | a) | sockets, 16 A, 250 V, Schuko type (side earth contacts), surface mounting (sm) | u | 30
9.16 | b) | sockets, 16 A, 5-pole, 380 V (sm) | u | 15
9.16 | c) | sockets, 25 A, 5 pole, 380 V (sm) | u | 20
9.16 | d) | 1plastic junction boxes, 100 mm x 100 mm, with internal terminals | u | 300
9.16 | e) | two-way switches, 16 A (sm) | u | 6
9.16 | f) | switches, 16 A (sm), 2-pole | u | 6
9.16 | g) | switches, 10 A (sm), 3- pole | u | 4
9.16 | h) | switches, 10 A (sm), 3-pole | u | 4
9.16 | i) | switches, 10 A (flush-mounted), 1-pole | u | 10
9.16 | j) | plastic junction boxes (flush-mounted) | u | 20
9.16 | k) | sockets, 16 A (flush-mounted) | u | 10
9.16 | l) | switches, push-button, 16 A (sm) | u | 12 |  |  | TOTAL 9 | 0
10. Coverings
10.1 |  | Cement mortar screed over slab, 3 cm | m2 | 100
10.2 | a) | 3 cm float finish screed over slab and mezzanine floor where PVC flooring is to be laid | m2 | 330
10.2 | b) | PVC covering, 2 mm tiles, incl. skirting and brass sills | m2 | 330
10.3 |  | Mortar-set vitreous glazed floor tiles 10 x 10 cm in plumbed rooms, incl. skirting | m2 | 100
10.4 |  | Adhesive-set white ceramic wall tiles, 15 x 15 cm | m2 | 170
10.5 |  | Hard concrete flooring, 4 cm | m2 | 1340
10.6 | a) | painting over plaster: preparation + 2 coats acrylic paint | m2 | 425
10.6 | b) | painting over pointed masonry, 2 coats of acrylic paint | m2 | 1410 |  | 0 | TOTAL 10 | 0 | 0 A |  |  | 0 | 0 |  | 2 | 0 | 0 |  | 0
|  | Please complete details below for Fees |  | Summary | [6 empty] | 0 | 55 | 52 |  |  | 55 | 52
|  | and representativity |  | Chapter | Total | A |  |  |  |  | 1 | 0 | 0 |  | 0 | 0 | 0
[11 empty] | Total | 55 | 52
|  |  |  | 1 | 0 | 0
|  |  |  | 2 | 0 | 0
|  |  |  | 3 | 0 | 0
|  |  |  | 4 | 0 | 0
|  |  |  | 5 | 0 | 0
|  |  |  | 6 | 0 | 0
|  |  |  | 7 | 0 | 0
|  |  |  | 8 | 0 | 0
|  |  |  | 9 | 0 | 0
|  |  |  | 10 | 0 | 0
|  |  |  | General Total | 0 | 0
ARCHITECT'S AND ENGINEER'S FEES (% of general total ) |  |  |  |  | 0 | 0
|  |  |  | TOTAL PRICE | 0 | 0
In your opinion is this Bill or variation representative? |  |  |  | (enter Y or N) | Y | Y
Information
The construction expert has decided NOT to price this BQ.
Note on K76: A reference 0, A, B, C shows that a price is required for the standard bill or one of the variants. The BQ total will not appear until all items have been priced. If the item price is included with another item, indicate which item in the Observations column. Insert a Zero in the unit price column to cancel the warning.